Microprocessor-Based Process Controllers

| Standard Spec. |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Model | TFC400 | TFC600 | TFC700 | TFC800 | TFC900 |  |
| Dimension | 48x48mm | 96x48mm | 72x72mm | 48x96mm | 96x96mm |  |
| Supply voltage | AC 85-265V,DC24V(Optional) |  |  |  |  |  |
| Frequency | 50/60HZ |  |  |  |  |  |
| Power Consumption | approx 3VA | approx 4VA | approx 3VA | approx 4VA | approx 4VA |  |
| Memory | Non-volatile memory E2 PROM |  |  |  |  |  |
| Input | Accuracy : 02%FS,Sample time : 250ms |  |  |  |  |  |
| TC | K, J, R, S, B, E, N, T, W5Re/W26Re,PL2,U,L |  |  |  |  |  |
| RTD | DPT100,JPT100,JPT50 |  |  |  |  |  |
| mA dc | 4~20ma,0~20ma |  |  |  |  |  |
| voltage dc | 0~1V, 0~5V, 0~10V, 1~5V, 2~10V -10~10mV, 0~10mV, 0~20mV, 0~50mV,10~50mV |  |  |  |  |  |
| DP Position | 0000,000.0,00.00,0.000 (available for mA or Voltage dc input) |  |  |  |  |  |
| Output1 | Main control output |  |  |  |  |  |
| Relay | SPST type | SPDT type | SPDT type | SPDT type | SPDT type |  |
| Voltage Pulse | For SSR drive. ON:24V . OF:0V . Maximum load current:20mA. |  |  |  |  |  |
| mA dc | 4~20ma,0~20ma.Maximum load resistance:560Ω |  |  |  |  |  |
| Voltage dc | 0~5V, 0~10V, 1~5V,2~10V. Maximum load current:20mA. |  |  |  |  |  |
| Alarm 1 | SPST type | SPDT type | SPST type | SPDT type | SPDT type |  |
|  | 3A, 220V, electrical life: 100,000 times or more (under the rated load). |  |  |  |  |  |
| Control algorithms | PID,P,PI,Pd,PD,ON/OFF(P=0),FUZZY |  |  |  |  |  |
| PID range | P:0~200%,I:0~3600 Secs,D:0~900 Secs |  |  |  |  |  |
| Isolation | Output terminal (control output , alarm transmissin)and input terminal are isolated separately. |  |  |  |  |  |
| Isolated resistance | 10M Ω or more between input terminals and case (ground) at DC 500V 10M Ω or more between output terminals and case (ground) at DC 500V |  |  |  |  |  |
| Dielectric strength | 1000V AC for 1 minute between input terminals and case (ground) 1500V AC for 1 minute between output terminals and case (ground) |  |  |  |  |  |
| Operation temperature | 0~50°C |  |  |  |  |  |
| Humidity range | 20~90% RH |  |  |  |  |  |
| Weight (approx) | approx 150g | approx 225g | approx 225g | approx 225g | approx 300g |  |
| Display Height | PV:7mm SV:7mm | PV:7mm SV:7mm | PV:14mm SV:10mm | PV:7mm SV:7mm | PV:14mm SV:10mm |  |

| Optional Spec. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Model | TFC400 | TFC600 | TFC700 | TFC800 | TFC900 |
| RAMP/SOAK Program | 2 patterns with 8 segments each. The two patterns can be linked together as 16 segments use |  |  |  |  |
| Output2 | For heating or cooling control use |  |  |  |  |
| Relay | SPST type | SPST type | SPST type | SPST type | SPST type |
| Voltage Pulse | For SSR drive. ON:24V . OF:0V . Maximum load current: 20mA. |  |  |  |  |
| mA dc | 4~20ma, 0~20ma.Maximum load resistance:560Ω |  |  |  |  |
| Voltage dc | 0~5V, 0~10V,1~5V, 2~10V. Maximum load current: 20mA. |  |  |  |  |
| Alarm 2 | SPST type | SPDT type | SPST type | SPDT type | SPDT type |
| Alarm 3 | None | SPST type | SPST type | SPST type | SPST type |
| Heater Break Alarm (HBA) | Display Range of Heater current:0.0~99.9A, Accuracy : 1%FS |  |  |  |  |
|  | Included CT: SC_80_T (5.8mm dia, 0.0~80.0A) or SC_100_T (12mm dia, 0.0~99.9A) |  |  |  |  |
|  | Alarm Relay : AL1 |  |  |  |  |
| Transmission | Available for PV or SV transmission |  |  |  |  |
| mA dc | 4~20ma,0~20ma.Maximum load resistance:560Ω |  |  |  |  |
| Voltage dc | 0~5V,0~10V,1~5V,2~10V. Maximum load current:20mA |  |  |  |  |
| Remote SV input | 4~20ma,0~20ma,O~5V,O~10V,1~5V,2~10V are available |  |  |  |  |
| Communication | protocol:MODBUS RTU,MODBUS ASCII,TAIE |  |  |  |  |
|  | interface:RS232,RS485,TTL |  |  |  |  |
|  | Baudrate:38400, 19200 ,9600, 4800 , 2400 bps. |  |  |  |  |
|  | 8 bit , Start bit , Parity : Odd oe Even , Stop bit : 1 or 2 bit |  |  |  |  |
| WaterProof / DustProof | IP65 |  |  |  |  |